## Slide 1: Fire Extinguisher Inspection
Step by Step Approach

## Slide 2: No obstruction to access or visibility

## Slide 3: Look to see if the indicator button is down.

## Slide 4: If the button is up remove the unit from service

## Slide 5: Visually inspect the hose and nozzle to ensure they are in good condition.

## Slide 6: Examine for obvious physical damage, corrosion, leakage, or clogged nozzle.

## Slide 7: Inspect the plunger and co2 cartridge.

## Slide 8: Remove the hose. Don’t worry if the tie has not been broken.

## Slide 9: Remove the black cover from the co2 cartridge

## Slide 10: Check for mud/coal or other material under the cover. Clean out any foreign material found.

## Slide 11: Remove the co2 cartridge.

## Slide 12: Left hand thread to remove.

## Slide 13: Check the foil seal.

## Slide 14: If the foil seal has been punctured remove the unit from service.

## Slide 15: Make sure plunger opening is clear of obstructions.

## Slide 16: Check action of plunger. Is it free? If not clean it out.

## Slide 17: Be sure to lift the plunger before replacing the co2 cartridge

## Slide 18: Replace the co2 cartridge.

## Slide 19: Replace the canister, black cover and hose.

## Slide 20: Visually inspect the extinguisher for dents, leaks, rust, chemical deposits or other signs of abuse/wear.

## Slide 21: Inspect the condition of the bottom of the fire extinguisher.
damage
rust
wear
abuse

## Slide 22: Examine wear spots. Are they substantial?
If the extinguisher is damaged or needs
recharging, remove it from service.

## Slide 23: Once the inspection is complete punch the tag in the correct location.

## Slide 24: Inspection of an internally charged fire ext.
Inspect for
damage
rust
wear

## Slide 25: The dial on the pressure gauge should be in the green zone or operable zone. If it is in the red zone, remove the unit from service.

## Slide 26: Make sure the pin is in place.

## Slide 27: Check for obstructions around actuator lever
Mud
dirt
coal

## Slide 28: Punch the tag in the correct location.

## Slide 29: Summary:
No obstructions
Actuator pin is up/dial is in operable zone
Hose, co2 canister, and housing are OK.
The inspection tag has been properly punched.
Thank You.